[image: image1.png]Charging a PbC® Battery Module

Using the profile depicted below, the PbC battery’s unique properties allow them to be fully charged from 100% DOD
within 5 hours once the maximum charge voltage has been reached. The minimum inrush current (initial current before
the battery reaches its maximum charging voltage) should be 0.4Cy,, though higher currents are recommended if
possible. Cio s the 10-hour current (the current that the battery can discharge for 10 hours). Once the voltage reaches
the limit of 13.5V for 12V models (18.0V for 16V models), or 2.25 volts per cell, the battery should be kept charging at
thatvoltage for 5 more hours to ensure ful capacity return.

Upon receipt of new batteries, it is suggested that each battery be “conditioned” prior to measurement and testing.
Conditioning protocol is a simple discharge to 3.6V for 12V models (4.8V for 16V models) at any discharge rate less than
or equal to C/1. Then recharge by the standard method described above.

Current Voltage

04Cr
minimum

——— 5 Hours ——
PbC battery charge profile

The recommended charge algorithm for PbC battery strings is a multi-step constant current charge outlined in row 1 on
the table below. Each step lasts until one battery reaches 13.5V for 12V modules (18.0V for 16 modules). As the steps
are completed, the batteries at lower SOC will begin to catch up to the batteries at higher SOC in the string. At this point
the batteries are ready to use. If the string is not to be used immediately, then the following periodic float charge
algorithm shown in row 2 on the table below should be employed. This serves the same purpose as float charging in
traditional VRLA string applications. It is recommended for when the string voltage drops below an average of the
nominal voltage of the individual modules in the string (12V or 16V depending on module used).

String Charge c/2 /5 /30
String Float Charge /10 /30 N/A

Because the PhC battery is a combination of lead-acid and super capacitor
technologies, the device exhibits a higher rate of self-discharge compared to
industry standard VRLA products, but the rate of discharge remains much
lower than that of super capacitors. Like other battery technologies,
however, the rate of self-discharge is directly impacted by the storage
temperature. It is recommended that all PbC batteries be stored at the
lowest possible temperature to ensure optimum energy retention and
extended shelf-life.

% Energy Remaining

ECE )
Open Circuit Storage Time (days)

Self-Discharge of PBC batteries in
percentage of energy remaining.




