Voltronic Power

Inverter and BMS 485 communication Protocol

Ellis/ Lory/ Jenny

2020/03/25

- BMS Pin Definition

1.1 BMS Card

|  | Definition |
| --- | --- |
| PIN 4 | RS485B |
| PIN 5 | RS485A |

1.2 Remote Box

|  | Definition |
| --- | --- |
| PIN 3 | RS485B |
| PIN 5 | RS485A |

- Communication parameter configuration

| Baud rate | Start bit | Data bit | Parity bit | Stop bit |
| --- | --- | --- | --- | --- |
| 9600 | 1 | 8 | N | 1 |

- Communication frame format

Device query command format

| Index | 1 | 2 | 3 |  | 4 |  | 5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Function | Slave ID | Command type | Start Address of data |  | Data Length |  | *CRC |  |
| Bytes | 1 | 1 | 2 |  | 2 |  | 2 |  |
|  | BMS address | Function code | MSB | LSB | MSB | LSB | LSB | MSB |

*The CRC check range is all of the bytes before the CRC field,

Command type table

| Index | Command type | Description |
| --- | --- | --- |
| 1 | 0x03 | Read Data |
| 2 | 0x10 | Write Data |

BMS normal response format

| Index | 1 | 2 | 3 |  | 4 |  | 5 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Function | Slave ID | Command type | Data Length |  | Data information |  | CRC |  |
| Bytes | 1 | 1 | 2 |  | Data length * 2 |  | 2 |  |
|  | BMS address | Function code | MSB | LSB | MSB | LSB | LSB | MSB |

BMS abnormal response format

| Index | 1 | 2 | 3 | 4 |
| --- | --- | --- | --- | --- |
| Function | Slave ID | Command type + 128 | Error code | CRC |
| Bytes | 1 | 1 | 1 | 2 |

Error code

| Index | Error code | Note |
| --- | --- | --- |
| 1 | 0x01 | Slave ID should be within 1~16. Slave ID error if out of range |
| 2 | 0x02 | Command type error if command didn’t exist, |
| 3 | 0x03 | CRC error |

- Command lists

4.1 Version information

| Data Address | Byte Size | Parameter | Parameter Unit |
| --- | --- | --- | --- |
| 0x0001 | 2 | Protocol type |  |
| 0x0002 | 2 | Protocol version |  |
| 0x0003 | 4 | BMS firmware version |  |
| 0x0005 | 4 | BMS hardware version |  |

4.2 BMS general status parameters inquiry

| Data Address | Byte Size | Parameter | Parameter Unit |
| --- | --- | --- | --- |
| 0x0010 | 2 | Number of cell: L | pcs |
| 0x0N11 | 2 | Cell N*20+1 voltage | 0.1V |
| 0x0N12 | 2 | Cell N*20+2 voltage |  |
| 0x0N13 | 2 | Cell N*20+3 voltage |  |
| 0x0N14 | 2 | Cell N*20+4 voltage |  |
| 0x0N15 | 2 | Cell N*20+5 voltage |  |
| 0x0N16 | 2 | Cell N*20+6 voltage |  |
| 0x0N17 | 2 | Cell N*20+7 voltage |  |
| 0x0N18 | 2 | Cell N*20+8 voltage |  |
| 0x0N19 | 2 | Cell N*20+9 voltage |  |
| 0x0N1A | 2 | Cell N*20+10 voltage |  |
| 0x0N1B | 2 | Cell N*20+11 voltage |  |
| 0x0N1C | 2 | Cell N*20+12 voltage |  |
| 0x0N1D | 2 | Cell N*20+13 voltage |  |
| 0x0N1E | 2 | Cell N*20+14 voltage |  |
| 0x0N1F | 2 | Cell N*20+15 voltage |  |
| 0x0N20 | 2 | Cell N*20+16 voltage |  |
| 0x0N21 | 2 | Cell N*20+17 voltage |  |
| 0x0N22 | 2 | Cell N*20+18 voltage |  |
| 0x0N23 | 2 | Cell N*20+19 voltage |  |
| 0x0N24 | 2 | *Cell N*20+20 voltage |  |
| 0x0025 | 2 | Number of temperature sensor: M | pcs |
| 0x0N26 | 2 | Temperature Sensor N*10+1 | 0.1K (Kelvin temperature) |
| 0x0N27 | 2 | Temperature Sensor N*10+2 |  |
| 0x0N28 | 2 | Temperature Sensor N*10+3 |  |
| 0x0N29 | 2 | Temperature Sensor N*10+4 |  |
| 0x0N2A | 2 | Temperature Sensor N*10+5 |  |
| 0x0N2B | 2 | Temperature Sensor N*10+6 |  |
| 0x0N2C | 2 | Temperature Sensor N*10+7 |  |
| 0x0N2D | 2 | Temperature Sensor N*10+8 |  |
| 0x0N2E | 2 | Temperature Sensor N*10+9 |  |
| 0x0N2F | 2 | Temperature Sensor N*10+10 |  |
| 0x0030 | 2 | Module charge current | 0.1A |
| 0x0031 | 2 | Module discharge current | 0.1A |
| 0x0032 | 2 | Module voltage | 0.1V |
| 0x0033 | 2 | SOC | % |
| 0x0034 | 4 | Module total capacity | mAH |

*If the parameter doesn’t exist, return 0x0000

4.3 BMS warning information inquiry

| Data Address | Byte Size | Parameter | Note |
| --- | --- | --- | --- |
| 0x0N40 | 2 | Number of cell: L |  |
| 0x0N41 | 2 | Cell N*20+1/ N*20+2 voltage state | 00H: normal 01H: below lower limit 02H: above higher limit F0H: other error |
| 0x0N42 | 2 | Cell N*20+3/ N*20+4 voltage state |  |
| 0x0N43 | 2 | Cell N*20+5/ N*20+6 voltage state |  |
| 0x0N44 | 2 | Cell N*20+7/ N*20+8 voltage state |  |
| 0x0N45 | 2 | Cell N*20+9/ N*20+10 voltage state |  |
| 0x0N46 | 2 | Cell N*20+11/ N*20+12 voltage state |  |
| 0x0N47 | 2 | Cell N*20+13/ N*20+14 voltage state |  |
| 0x0N48 | 2 | Cell N*20+15/ N*20+16 voltage state |  |
| 0x0N49 | 2 | Cell N*20+17/ N*20+18 voltage state |  |
| 0x0N4A | 2 | Cell N*20+19/ N*20+20 voltage state |  |
| 0x0050 | 2 | Number of temperature sensor: M |  |
| 0x0N51 | 2 | BMS Temperature N*10+1/ N*10+2 state | 00H: normal 01H: below lower limit 02H: above higher limit F0H: other error |
| 0x0N52 | 2 | BMS Temperature N*10+3/ N*10+4 state |  |
| 0x0N53 | 2 | BMS Temperature N*10+5/ N*10+6 state |  |
| 0x0N54 | 2 | BMS Temperature N*10+7/ N*10+8 state |  |
| 0x0N55 | 2 | BMS Temperature N*10+9/ N*10+10 state |  |
| 0x0060 | 2 | Module charge voltage state | 00H: normal 01H: below lower limit 02H: above higher limit F0H: other error |
| 0x0061 | 2 | Module discharge voltage state |  |
| 0x0062 | 2 | Cell charge voltage state |  |
| 0x0063 | 2 | Cell discharge voltage state |  |
| 0x0064 | 2 | Module charge current state |  |
| 0x0065 | 2 | Module discharge current state |  |
| 0x0066 | 2 | Module charge temperature state |  |
| 0x0067 | 2 | Module discharge temperature state |  |
| 0x0068 | 2 | Cell charge temperature state |  |
| 0x0069 | 2 | Cell discharge temperature state |  |

*If the parameter didn’t exist, return 0x0000

4.4 BMS charger and discharge information inquiry

| Data Address | Byte Size | Parameter | Parameter Unit |
| --- | --- | --- | --- |
| 0x0070 | 2 | Charge voltage limit | 0.1V |
| 0x0071 | 2 | Discharge voltage limit | 0.1V |
| 0x0072 | 2 | Charge current limit | 0.1A |
| 0x0073 | 2 | Discharge current limit | 0.1A |
| 0x0074 | 2 | Charge, discharge status |  |

Charge, discharge status:

| Bit |  | Content |  | Note |  |
| --- | --- | --- | --- | --- | --- |
| 7 |  | Charge enable |  | 1: yes 0: request stop charge |  |
| 6 |  | Discharge enable |  | 1: yes 0: request stop discharge |  |
| 5 |  | Charge immediately |  | 1: request: 0: no request |  |
| 4 |  | Charge immediately2 |  | 1: request: 0: no request |  |
| 3 |  | Full charge request |  | 1: request: 0: no request |  |
| 2 |  |  |  |  |  |
| 1 |  |  |  |  |  |
| 0 |  |  |  |  |  |
| 0x0075 | 4 |  | Run time to empty |  | S |

*Bit 5: Set when SoC is very low, like 5~9%, device need charge immediately until this flag disappear.

*Bit 4: Set when SoC is low, like 10~14%, it will be better that device charge immediately until this flag disappear.

*Bit 3: Set when BMS need device fully charged.